## Manufacturers sheet
PV inverter evaluation for rooftop PV systems in the Sultanate of Oman |  |  |  | Version 02 / 03 June 2019
No. | Item | Requirement | Actual value/ appearance | Your Response
Company / Contact:
1 | Inverter type and Manufacturer
1.1* | What type(s) of inverter will be delivered ? | Clear type designation is required; a special type for desert climate is preferred | Provide the type designation
Is a special type for desert climate available?
1.2 | Would you like to point out special features / new developments / improvements to us? | For example, special housing material, effective cooling, less power derating efficiency etc.
1.3 | Does the inverter manufacturer have a subsidary, | Contact person or office in Oman/Middle East area
| office or representative in Oman or at least |  | Provide contact
in the Middle East area?
1.4* | Can the inverter manufacturer indicate reference projects with the offered inverter type(s) at point 1.1. or at least similar own products? | Experience and reference projects in | Provide reference projects minimum data: Country, Nominal Power, inverter type(s), commissioning data
Near or Middle East (alternatively in other hot climate areas)
2 | PV Inverter electrical characteristics
2.1* | Please state the Maximum Efficiency. | Minimum value of 97% are required.
2.2 | Please state the European Efficiency.
2.3 | Has the efficiency for maximum power point tracking - MPPT of the inverter been specified? | Efficiency certificate according EN 50530:2010 + A1:2013 (Total efficiency for MPPT)
Provide a copy
2.4 | Which MPP voltage range (DC) is usable? | A wide range is better for individual solutions.
2.5 | What is the system voltage (AC)? | Low voltage grid 240/415 V
2.6 | Please specify the efficiency deviation for different MPP- voltages. | Detailed information about efficiencies for different MPP voltages (e.g. curves) are desired.
2.7 | What is the operating temperature range? | Ambient temperatures up to 55 °C are possible.
2.8 | Please specify the power derating at high operating temperatures? What is the maximum temperature without power derating? | Inverters must be designed for ambient temperatures up to 50 °C. Derating effect should occur starting from temperatures above 45 °C.
2.9* | What is the specified International protection class (IPxx)? | International protection classes according to IEC 60529. If the inverter is installed outdoors, IP class 65 must be observed.
Provide a copy
3 | Inverter safety, grid connection, Electromagnetic Compatibility (EMC), Certification
3.1* | Are the safety requirements for inverters met ? | Valid certification to the international standard IEC 62109-1/-2 is required. |  |  | OK?
|  | Part 1: General requirements | Provide a copy
Part 2: Particular requirements for inverters
3.2 | Does certification process include a regular production site inspection (IEC 62109) ? | Factory Inspection according to CIG 023 (Product quality and product safety assessment)
OK?
3.3 | Has the technical specification of the performance of LVRT (Low Voltage Ride Through) functions in the inverter been evaluated? | Inverters in power distribution systems - Test methods for LVRT measures (IEC/TS 62910:2015) - valid certificate to the international standard is required. | Provide a copy
3.4* | Has the Electromagnetic Compatibility (EMC) confirmed? | Valid certification to international standard IEC/EN 61000 series
Provide a copy
3.5* | Have test procedures to evaluate the performance of islanding prevention measures used with utility-interconnected PV systems been performed? | Valid certificate to the international standard IEC 62116:2014
Provide a copy
3.6 | Can you specify for your firmware the compliance with Functional Safety Standard? | Compliance with IEC/EN 60730-1 or UL 1998, etc.
3.7 | Which communication interfaces are usable? | RS485, Bluetooth, Webconnect interfaces, multifunction relays for various inverters, USB, WiFi-WLan, LAN interface…
3.8 | Do you provide a comminication internet portal? | Performance data, statistics, information on software versions, assistance for the user.
3.9 | Statusindicator, information display or error message? | The inverter should provide information about the current status at any time, e.g. LED status indicators, error messages, performance data…
4 | Warranties
4.1 | What is your warranty period? | Warranties given by manufacturer (standard and options for longterm)
4.2 | Which performance restrictions and exclusions do apply? | What limits in field of use and exclusions are valid? - Are coastal site areas excluded? What does this mean for the required minimum distance to the sea? - Other relevant restrictions | Provide warranty conditions
4.3 | Is an exchange service in case of failure guaranteed?
5 | Documentation of the Inverter
5.1* | Are all relevant information on the name plate to meet the requirements of IEC 62109-1 and DIN EN 50524? | Required data: - Identification of manufacturer and component - Electrical parameter - Protection and safety classes - Ambient conditions | Provide a picture or copy
5.2* | Is a datasheet with the relevant information to meet the reqirements of IEC 62109-1 available? |  | Provide a copy
5.3* | Is a manual available what meets the requirements of IEC 62109 ? | - Are clear mounting guideline, tools and necessesary equipment described?
|  | - Are maintenance procedures described? | Provide a copy
- Is a service contact given?
6 | Quality and Environment Management in inverter production
6.1 | Has the manufacturer a certified QM according to ISO 9001? |  | Provide a copy
6.2 | Has the company a certified environmental management system established? | Is a valid certificate ISO 14001 or other enevironmental certificate available? | Provide a copy
6.3 | Has the company an occupational health and safety management system established? | Is a valid certificate for occupational health and safety management available, e.g. OHSAS 18001:2017 or ISO 45001:2018 | Provide a copy
6.4 | Is a FAT (Factory Acceptance Test) carried out? |  | Provide criteria or a copy
* | This is an obligatory requirement (Non-compliance is an exclusion criterion)